LISTADO DE INSTRUMENTOS

No part of this document may be reproduced or transmitted in any way or stored in any retrieval system without written permission of THE AUTHORS

|  | Revision | Prepared |  | Checked |  | Approval |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. |  | By | Date | By | Date | By | Date |
| 0 | First Issue | HRI | 07/07/04 | HRI | 07/07/04 | SEG | 07/07/04 |
| 0 | Second Issue | HRI | 08/11/04 | HRI | 08/11/04 | SEG | 08/11/04 |

# Listado Emerson - ASCO

# Controlador de Nivel

- Modelo: 2088G2S22A1E5

- Cantidad: 2

- Tag: LT01-ISS y LT02-ISS

# Transmisor de Presión

- Modelo: 2088G2S22A1E5

- Cantidad: 1

- Tag: PT03-ISS

# Transmisor de Temperatura

- Modelo: 248HAE5U2URT25U004

- Cantidad: 2

- Tag: TT02-ISS y TT03-ISS

# Solenoides

- Modelo: S/cuadro página 4 y 5.

- Cantidad: 33

- Tag: S/cuadro página 4 y 5.

# Transmisor de Conductividad

- Modelo: 228-02-21-56-61

- Cantidad: 2

- Tag: CT-001 y CT-002

# Unidad de Gobierno

| Linea | Cant | Fluido | TAG | Presión max | Presión min | Vol | Delta P | Kv | diam | Material de sello y disco | Obs. | Montaje |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | bar (g) | bar (g) | m3/h | bar |  |  |  |  |  | modelo | volts(DC) | cuerpo | sellos | conex. | kv |
| 1 | 2 | Aceite vegetal | SV-01/02 | 0.12 | 0.02 | 0.1 | 0.01 | 1 | 1/2 | Vitón | NC | Horizontal | EF8210G094V | 24 | Latón | VITON | 1/2 | 3.4 |
| 2 | 2 | Metóxido | SV-03/04 | 0.025 | 0.005 | 0.15 | 0.005 | 1.9 | 1/2 | Vitón | Considerar solución de Hidróxido de Sodio, NC | 1 Horizontal y 1 Vertical | EF8210C087V | 24 | AISI 304 | VITON | 1/2 | 3.4 |
| 3 | 1 | Biodiesel | SV-05 | 0.4 | 0.2 | 0.1 | 0.05 | 0.4 | 1/2 | Pref. Teflon. Alt. Vitón | NC | Horizontal | EF8262G038T | 24 | AISI 304 | PTFE | 1/4 | 0.82 |
| 4 | 1 | Agua | SV-06 | 0.4 | 0.2 | 0.85 | 0.08 | 3 | 1/2 | NBR o PTFE | NC | Horizontal | EF8210G094 | 24 | Latón | NBR | 1/2 | 3.4 |
| 5 | 1 | Biodiesel | SV-07 | 0.4 | 0.2 | 0.98 | 0.08 | 3 | 1/2 | Pref. Teflon. Alt. Vitón | NC | Horizontal | EF8210C087V | 24 | AISI 304 | VITON | 1/2 | 3.4 |
| 6 | 1 | Acido Acet. | SV-08 | 0.01 | 0.01 | 0.03 | 0.01 | 0.3 | 1/4 | Neopreno | NC | Horizontal | EF8262G038E | 24 | AISI 304 | EPDM | 1/4 | 0.82 |
| 7 | 3 | Agua | SV-09/10/11 | 0.25 | 0.05 | 0.06 | 0.01 | 0.6 | 1/4 | NBR o PTFE | NC | Vertical | EF8262G090 | 24 | Latón | NBR | 1/4 | 0.82 |
| 8 | 2 | Agua | SV-12/13 | 0.25 | 0.05 | 0.06 | 0.01 | 0.6 | 1/4 | NBR o PTFE | NC | Horizontal | EF8262G090 | 24 | Latón | NBR | 1/4 | 0.82 |
| 9 | 1 | Agua | SV-14 | 0.25 | 0.05 | 0.06 | 0.01 | 0.6 | 1/4 | NBR o PTFE | NC | Horizontal | EF8262G090 | 24 | Latón | NBR | 1/4 | 0.82 |
| 10 | 2 | Glicerina | SV-15/16 | 0.15 | 0.05 | 0.6 | 0.05 | 3 | 1/2 |  | NC | Vertical | EF8210G094 | 24 | Latón | NBR | 1/2 | 3.4 |
| 10 | 2 | Glicerina | SV-17/18 | 1 | 0.15 | 0.85 | 0.1 | 3 | 1/2 |  | NC | Horizontal | EF8210G094 | 24 | Latón | NBR | 1/2 | 3.4 |
| 11 | 1 | Aire | SV-19 | 1 | 0.1 | 80 | 0.8 | 2.5 | 1/2 | Buna N | NA | Vertical | EF8210G034 | 24 | Latón | NBR | 1/2 | 3.4 |
| 12 | 1 | Metanol | SV-20 | 1.5 | 0.1 | 20 | 0.1 | 1.1 | 1/4 | EPDM | NA | Vertical | EF8262G038E | 24 | AISI 304 | EPDM | 1/4 | 0.82 |
| 13 | 1 | Aire | SV-21 | 1 | 0.1 | 80 | 0.8 | 2.5 | 1/2 | Buna N | NA | Vertical | EF8210G034 | 24 | Latón | NBR | 1/2 | 3.4 |
| 14 | 1 | Aire | SV-22 | 1 | 0.1 | 80 | 0.8 | 2.5 | 1/2 | Buna N | NA | Vertical | EF8210G034 | 24 | Latón | NBR | 1/2 | 3.4 |
| 15 | 1 | Aire | SV-23 | 1 | 0.1 | 80 | 0.8 | 2.5 | 1/2 | Buna N | NA | Vertical | EF8210G034 | 24 | Latón | NBR | 1/2 | 3.4 |
| 16 | 1 | Aire | SV-24 | 1 | 0.1 | 80 | 0.8 | 2.5 | 1/2 | Buna N | NA | Vertical | EF8210G034 | 24 | Latón | NBR | 1/2 | 3.4 |
| 17 | 4 | Agua + Det | SV-25/26/27/28 | 2 | 0.25 | 3 | 1 | 3 | 1/2 | NBR o PTFE | NC | Horizontal | EF8210G094 | 24 | Latón | NBR | 1/2 | 3.4 |
| 18 | 1 | Aire | SV-29 | 2 | 0.1 | 30 | 0.1 | 2 | 1/2 | NBR o PTFE | NA | Vertical | EF8210G034 | 24 | Latón | NBR | 1/2 | 3.4 |
| 19 | 1 | Aceite vegetal | SV-30 | 0.05 | 0.002 | 0.3 | 0.01 | 2.6 | 1/2 | Vitón | Entrada de Aceite, NC | Vertical | EF8210G094 | 24 | Latón | NBR | 1/2 | 3.4 |
| 20 | 1 | Metanol | SV-31 | 0.05 | 0.002 | 0.3 | 0.01 | 2.7 | 1/2 | EPDM | Entrada de Metanol, NC | Horizontal | EF8210G087E | 24 | AISI 304 | EPDM | 1/2 | 3.4 |
| 21 | 2 | Agua | SV-32/33 | 0.4 | 0.2 | 0.85 | 0.08 | 3 | 1/2 | NBR o PTFE | NA | Horizontal | EF8210G034 | 24 | Latón | NBR | 1/2 | 3.4 |