## LT01_ISS
[5 empty] | Pressure Transmitter |  | Sheet |  | of
Client | UBA |  |  |  | Specification |  | Spec No. |  | Rev.
Project | BIODIESEL | [5 empty] | Contract |  | P.O.
Unit | [6 empty] | Req. |  | BY
Location | [6 empty] | CHK'D |  | APPR.
|  | 1 | Tag No. |  | LT01
GENERAL |  | 2 | Description of Service | OIL
|  | 3 | PID No.
[5 empty] | Minimum | Operating | Maximum | Design | Unit
SERVICE |  | 4 | Pressure |  | 1 | 1 | 1 | 2 | kg/cm2-g
CONDITIONS |  | 5 | Process Temperature |  | 5 | 20 | 40 | 80 | C
|  | 6 | Ambient Temperature |  | 0 | 20 | 40 |  | C
|  | 7 | Manufacturer |  | Rosemount
|  | 8 | Model No. |  | 2088G2S22A1E5
|  | 9 | Pressure Transmitter Type |  | Gage Pressure
|  | 10 | Calibrated Span |  | 0 | - | 150 |  | psig
TRANSMITTER |  | 11 | Adjustable Range |  | 0.00-15.00 to 0.00-150.00 psi
|  | 12 | Output Signal |  | 4-20 mA dc/Digital HART Protocol
|  | 13 | Body Rating
|  | 14 | Process Flange Type |  | Gage Pressure Transmitter
|  | 15 | Drain/Vent
|  | 16 | Process Flange
|  | 17 | Adapters
BODY |  | 18 | Wetted O-ring
|  | 19 | Housing
|  | 20 | Bolts
|  | 21 | Mounting Brackets
|  | 22 | Conduit Entry Size
ELEMENT |  | 23 | Isolating Diaphragm |  | 316L SST
|  | 24 | Fill Fluid
|  | 25 | Cert/Approval Type |  | FM Explosion-Proof Approval
|  | 26 | Meter
|  | 27 | Zero and Span Adjust
OPTIONS |  | 28 | Custom Configuration
|  | 29 | Transient Protection
|  | 30 | Manufacturer
|  | 31 | Model No.
MANIFOLD |  | 32 | Manifold Style
|  | 33 | Manifold Type
34
35
NOTES |  | 36
37
This report is provided according to the terms and conditions of the Instrument Toolkit(TM) End-Use Customer License Agreement.
Version: 3.0 (Build109B) | [5 empty] | Printed On: | 2026-07-30 05:12 | 46233.2163

## LT02_ISS
[5 empty] | Pressure Transmitter |  | Sheet |  | of
Client | UBA |  |  |  | Specification |  | Spec No. |  | Rev.
Project | BIODIESEL | [5 empty] | Contract |  | P.O.
Unit | [6 empty] | Req. |  | BY
Location | [6 empty] | CHK'D |  | APPR.
|  | 1 | Tag No. |  | LT02
GENERAL |  | 2 | Description of Service | METOXIDO
|  | 3 | PID No.
[5 empty] | Minimum | Operating | Maximum | Design | Unit
SERVICE |  | 4 | Pressure |  | 1 | 1.2 | 1.5 | 2 | kg/cm2-g
CONDITIONS |  | 5 | Process Temperature |  | 10 | 48 | 65 | 120 | C
|  | 6 | Ambient Temperature |  | 0 | 20 | 35 |  | C
|  | 7 | Manufacturer |  | Rosemount
|  | 8 | Model No. |  | 2088G2S22A1E5
|  | 9 | Pressure Transmitter Type |  | Gage Pressure
|  | 10 | Calibrated Span |  | 0 | - | 150 |  | psig
TRANSMITTER |  | 11 | Adjustable Range |  | 0.00-15.00 to 0.00-150.00 psi
|  | 12 | Output Signal |  | 4-20 mA dc/Digital HART Protocol
|  | 13 | Body Rating
|  | 14 | Process Flange Type |  | Gage Pressure Transmitter
|  | 15 | Drain/Vent
|  | 16 | Process Flange
|  | 17 | Adapters
BODY |  | 18 | Wetted O-ring
|  | 19 | Housing
|  | 20 | Bolts
|  | 21 | Mounting Brackets
|  | 22 | Conduit Entry Size
ELEMENT |  | 23 | Isolating Diaphragm |  | 316L SST
|  | 24 | Fill Fluid
|  | 25 | Cert/Approval Type |  | FM Explosion-Proof Approval
|  | 26 | Meter
|  | 27 | Zero and Span Adjust
OPTIONS |  | 28 | Custom Configuration
|  | 29 | Transient Protection
|  | 30 | Manufacturer
|  | 31 | Model No.
MANIFOLD |  | 32 | Manifold Style
|  | 33 | Manifold Type
34
35
NOTES |  | 36
37
This report is provided according to the terms and conditions of the Instrument Toolkit(TM) End-Use Customer License Agreement.
Version: 3.0 (Build109B) | [5 empty] | Printed On: | 2026-07-30 05:12 | 46233.2163

## PT03_ISS
[5 empty] | Pressure Transmitter |  | Sheet |  | of
Client | UBA |  |  |  | Specification |  | Spec No. |  | Rev.
Project | BIODIESEL | [5 empty] | Contract |  | P.O.
Unit | [6 empty] | Req. |  | BY
Location | [6 empty] | CHK'D |  | APPR.
|  | 1 | Tag No. |  | PT03
GENERAL |  | 2 | Description of Service | BIODIESEL
|  | 3 | PID No.
[5 empty] | Minimum | Operating | Maximum | Design | Unit
SERVICE |  | 4 | Pressure |  | -0.5 | 1.2 | 1.5 | 2 | kg/cm2-g
CONDITIONS |  | 5 | Process Temperature |  | 5 | 50 | 65 | 120 | C
|  | 6 | Ambient Temperature |  | 0 | 25 | 35 |  | C
|  | 7 | Manufacturer |  | Rosemount
|  | 8 | Model No. |  | 2088G2S22A1E5
|  | 9 | Pressure Transmitter Type |  | Gage Pressure
|  | 10 | Calibrated Span |  | 0 | - | 150 |  | psig
TRANSMITTER |  | 11 | Adjustable Range |  | 0.00-15.00 to 0.00-150.00 psi
|  | 12 | Output Signal |  | 4-20 mA dc/Digital HART Protocol
|  | 13 | Body Rating
|  | 14 | Process Flange Type |  | Gage Pressure Transmitter
|  | 15 | Drain/Vent
|  | 16 | Process Flange
|  | 17 | Adapters
BODY |  | 18 | Wetted O-ring
|  | 19 | Housing
|  | 20 | Bolts
|  | 21 | Mounting Brackets
|  | 22 | Conduit Entry Size
ELEMENT |  | 23 | Isolating Diaphragm |  | 316L SST
|  | 24 | Fill Fluid
|  | 25 | Cert/Approval Type |  | FM Explosion-Proof Approval
|  | 26 | Meter
|  | 27 | Zero and Span Adjust
OPTIONS |  | 28 | Custom Configuration
|  | 29 | Transient Protection
|  | 30 | Manufacturer
|  | 31 | Model No.
MANIFOLD |  | 32 | Manifold Style
|  | 33 | Manifold Type
34
35
NOTES |  | 36
37
This report is provided according to the terms and conditions of the Instrument Toolkit(TM) End-Use Customer License Agreement.
Version: 3.0 (Build109B) | [5 empty] | Printed On: | 2026-07-30 05:12 | 46233.2163

## TT02_ISS
|  |  | RTD Assembly |  | Sheet |  | of
Client |  | UBA | W/ Thermowell |  | Spec No. |  | Rev.
Project |  | BIODIESEL | Specification Sheet |  | Contract |  | P.O.
Unit |  |  |  |  | Req. |  | BY
Location |  |  |  |  | CHK'D |  | APPR.
| 1 | Tag No. | TT02
GENERAL | 2 | Description of Service | METOXIDO
| 3 | PID No./Line Number
|  |  | Minimum | Normal | Maximum | Design |  | Unit
PROCESS | 4 | Pressure | 1 | 1.2 | 1.5 | 2 |  | kg/cm2-g
CONDITIONS | 5 | Process Temperature | 10 | 48 | 65 | 120 |  | C
| 6 | Ambient Temperature | 0 | 20 | 35 |  |  | C
| 7 | Manufacturer/Model Number | 248HAE5U2URT25U004
| 8 | Product Description | Smart DIN B Head Mount Temperature Transmitter
| 9 | Connection Head Material, IP Rating, Connection Thread | Universal Connection Head, DIN IP68, Aluminum
RTD | 10 | Sensor Lead Wire Termination | Pt 100 RTD 1/2 inch Adapter, Spring load 4-Wire, Single
Element, ASTM
SENSOR | 11 | Sensor Type | Pt 100 RTD 1/2 inch Adapter, Spring load 4-Wire, Single
Element, ASTM
| 12 | Extension Type/Material | [NULL]
| 13 | Instrument Connection Thread | 1/2-inch NPT
| 14 | Extension Length | None
| 15 | Sensor Length
| 17 | Thermowell Material | Machined Tapered Barstock Thermowell Process Connection, 316L
-1.4404
| 18 | Thermowell Immersion Length | 4.0 inch
| 19 | Thermowell Lagging Length
THERMOWELL | 20 | Thermowell Construction Style
| 21 | Thermowell Process Connection | Thread mount, 3/4 inch NPT
| 22 | Thermowell Stem Style | Thread mount, 3/4 inch NPT
| 23 | Thermowell Mounting
| 24 | Flange Type/Rating/Material
| 25 | Lead Wire Extensions
OPTIONS | 26 | Mounting Adapters
| 27 | Cert/Approval Type | FM explosion proof
| 28 | Sensor to Transmitter Matching
| 29 | Calibration | None
| 30 | Class A Sensor
| 31 | Ring Joint Flange Face
| 32 | Pressure Testing | None
| 33 | Material Certification | None
| 34 | Dye Penetration Testing
| 35 | Cleaning
| 36 | Tagging
| 37 | Approval | FM explosion proof
| 38 | Assemble to Transmitter | Yes
| 39 | Plug and Chain
| 40 | Full-Penetration Weld
MOUNTING | 41 | Extension Fitting Assemblies
ACCESSORIES | 42 | Connection Head
38
39
NOTES | 40
41
This report is provided according to the terms and conditions of the Instrument Toolkit(TM) End-Use Customer License Agreement.
Version: 3.0 (Build109B) |  | Printed On: | 2026-07-30 05:12

## TT03_ISS
|  |  | RTD Assembly |  | Sheet |  | of
Client |  | UBA | W/ Thermowell |  | Spec No. |  | Rev.
Project |  | BIODIESEL | Specification Sheet |  | Contract |  | P.O.
Unit |  |  |  |  | Req. |  | BY
Location |  |  |  |  | CHK'D |  | APPR.
| 1 | Tag No. | TT03
GENERAL | 2 | Description of Service | BIODIESEL
| 3 | PID No./Line Number
|  |  | Minimum | Normal | Maximum | Design |  | Unit
PROCESS | 4 | Pressure | -0.5 | 1.2 | 1.5 | 2 |  | kg/cm2-g
CONDITIONS | 5 | Process Temperature | 5 | 50 | 65 | 120 |  | C
| 6 | Ambient Temperature | 0 | 25 | 35 |  |  | C
| 7 | Manufacturer/Model Number | 248HAE5U2URT25U004
| 8 | Product Description | Smart DIN B Head Mount Temperature Transmitter
| 9 | Connection Head Material, IP Rating, Connection Thread | Universal Connection Head, DIN IP68, Aluminum
RTD | 10 | Sensor Lead Wire Termination | Pt 100 RTD 1/2 inch Adapter, Spring load 4-Wire, Single
Element, ASTM
SENSOR | 11 | Sensor Type | Pt 100 RTD 1/2 inch Adapter, Spring load 4-Wire, Single
Element, ASTM
| 12 | Extension Type/Material | [NULL]
| 13 | Instrument Connection Thread | 1/2-inch NPT
| 14 | Extension Length | None
| 15 | Sensor Length
| 17 | Thermowell Material | Machined Tapered Barstock Thermowell Process Connection, 316L
-1.4404
| 18 | Thermowell Immersion Length | 4.0 inch
| 19 | Thermowell Lagging Length
THERMOWELL | 20 | Thermowell Construction Style
| 21 | Thermowell Process Connection | Thread mount, 3/4 inch NPT
| 22 | Thermowell Stem Style | Thread mount, 3/4 inch NPT
| 23 | Thermowell Mounting
| 24 | Flange Type/Rating/Material
| 25 | Lead Wire Extensions
OPTIONS | 26 | Mounting Adapters
| 27 | Cert/Approval Type | FM explosion proof
| 28 | Sensor to Transmitter Matching
| 29 | Calibration | None
| 30 | Class A Sensor
| 31 | Ring Joint Flange Face
| 32 | Pressure Testing | None
| 33 | Material Certification | None
| 34 | Dye Penetration Testing
| 35 | Cleaning
| 36 | Tagging
| 37 | Approval | FM explosion proof
| 38 | Assemble to Transmitter | Yes
| 39 | Plug and Chain
| 40 | Full-Penetration Weld
MOUNTING | 41 | Extension Fitting Assemblies
ACCESSORIES | 42 | Connection Head
38
39
NOTES | 40
41
This report is provided according to the terms and conditions of the Instrument Toolkit(TM) End-Use Customer License Agreement.
Version: 3.0 (Build109B) |  | Printed On: | 2026-07-30 05:12